|  | Petroleum Tank Release Compliance Checklist Petroleum Remediation Program Doc Type: Petrofund Compliance Checklist |
| --- | --- |

| Site name: | Junction Oasis |  |  | LEAK000: | 20296 |
| --- | --- | --- | --- | --- | --- |
| MPCA Project Manager: |  | Amy Miller |  | Date review completed: | 8/23/2017 |
| Regional MPCA Tank Inspector (if applicable): |  |  | Jeff Brandon | Date review completed: | 8/21/2017 |
|  |  |  |  |  | (mm/dd/yyyy) |

Instructions:	Project Manager – Complete Section I, plus remaining applicable sections only if Tank Inspector does not.

# Tank Inspector – Complete Section II, plus Sections III and IV if applicable. No Tank Inspector review needed on unregulated tank sites. Section III and IV evaluations should be based on time period current Petrofund applicant was responsible for tank controls. Send this completed form to the site Project Manager within five days of receiving the Petrofund application from the Department of Commerce.

I.	General Information (all sites)

Release notification:

| Date release discovered: | 10/12/2016 |  |  | Date release reported: | 10/13/2016 |
| --- | --- | --- | --- | --- | --- |
| When/how was release discovered (if inadequate)? |  |  | tank removal |  |  |
| Was there environmental damage due to delay (if inadequate)? Yes No |  |  |  |  |  |
| Adequate or Inadequate |  | Recommended reduction? Yes No |  |  |  |

Status of responsible party:

| Regular applicant Limited use applicant |  |
| --- | --- |
| Cooperation issues: Yes No (If yes, please prepare a narrative to be appended to the Commissioner’s Site Report.) |  |
| Comments: |  |

II.	Tank Information (all sites)

Unregulated Tank(s):  Underground Storage Tanks (USTs) 110 gallons or less; or Aboveground Storage Tanks (ASTs) 500 gallons or less; or ASTs between 500 - 1,100 gallons if they are greater than 500 feet from surface water; or residential (for non-commercial purposes) and heating oil ASTs/USTs 1,100 gallons or less; or farm USTs 1,100 gallons or less; or any farm AST, regardless of size if used for farming purposes; or ASTs that are on site for less than 30 days (regardless of size).

State Regulated Tank(s):  Heating oil USTs with a capacity more than 1,100 gallons or all ASTs not specified above.

Federally Regulated Tank(s):  All USTs not specified above.

III.	State Tanks/Federal Tanks

Corrosion protection:

Tanks:     Yes     No      N/A	Piping:     Yes     No      N/A

Required on steel piping/steel USTs installed on or after August 1, 1985. Steel piping/steel USTs installed before August 1, 1985, require corrosion protection by December 22, 1998, except heating oil USTs installed before August 1, 1985, which don’t ever require corrosion protection. Does not apply to ASTs (they require corrosion protection by November 1, 2003, but are not subject to a reduction). Violations which occurred before December 22, 1998, should be cited as inadequate but not recommended for reduction.

Adequate  or   Inadequate	Recommend Reduction?     Yes     No

AST Secondary Containment:     Yes     No      N/A

Applicable only for dikes or other structures that would contain a spill as required by Minn. R. 7151.6400, subp. 1B (Supp. 1998). Does not apply to impervious liners or other AST safeguards. Violations which occurred prior to November 1, 1998, should be cited as inadequate but not recommended for reduction.

Adequate  or   Inadequate	Recommend Reduction?     Yes     No

IV.	Federal Tanks

Spill prevention:	 Yes     No      N/A

Required on USTs installed on or after December 22, 1988.  USTs installed before December 22, 1988, require spill prevention by December 22, 1998. Violations which occured prior to December 22, 1998, should be cited as inadequate but not recommended for reduction.

Adequate  or   Inadequate	Recommend Reduction?     Yes     No

Overfill protection:	 Yes     No      N/A

Required on USTs installed on or after December 22, 1988.  USTs installed before December 22, 1988, require spill protection by December 22, 1998. Violations which occured prior to December 22, 1998, should be cited as inadequate but not recommended for reduction.

Adequate  or   Inadequate	Recommend Reduction?     Yes     No

Leak detection:

Tanks:	Tank leak detection:	 Yes     No      N/A

Adequate  or   Inadequate	Recommend Reduction?     Yes     No

| If tank was installed: | Then the leaks detection deadline is: |
| --- | --- |
| Before 1965 or unknown | 12/22/1989 |
| 1965 – 1969 | 12/22/1990 |
| 1970 – 1974 | 12/22/1991 |
| 1975 – 1979 | 12/22/1992 |
| 1980 – 12/22/88 | 12/22/1993 |

(Tanks installed after 12/22/1988 should have leak detection at installation.)

Piping:	Pipe leak detection:	 Yes     No      N/A

Adequate  or   Inadequate	Recommend Reduction?     Yes     No

(Applicable for pressurized piping installed after December 22, 1988. Pressurized piping installed before December 22, 1988 must have leak detection by December 22, 1990.)

Violations which occurred before December 22, 1993, should be cited as inadequate but not recommended for reduction.

Enforcement actions taken by Tank Compliance and Enforcement Unit?     Yes     No

Describe enforcement actions including dates and monetary penalties. Insert any other comments regarding inadequate sections:

MPCA issued three citation warnings. April 2008 for CP violations - failed to test and failed to repair the CP system. November 2010 for CP violations - failed to repair CP system. September 2013 for spill prevention - four spill buckets have cracks and holes. Recommend a reduction.