APPLICABILITY OF NSPS SUBPART Kb and STATE STANDARD OF PERFORMANCE FOR TANKS		2-6-19

The tables and information in this document can be used to gather the necessary information to determine rule applicability, compliance and populate the Tempo database. It is acceptable to request that the Permittee fill out the tables. Often they will want to know what can help the project schedule, and they could assist by filling this out for you. The following information is provided in this document:

- Sample TSD language

- Table 1: 40 CFR § 60.110b(a) Applicability and Exemptions (table to determine NSPS applicability)

- Table 2: 40 CFR § 60.112b(a) Standard for VOC requiring a floating roof (to determine if floating roof needed)

- Table 3: 40 CFR § 60.112xx Tank Seal Description and NSPS Inspections

- Table 4: Minnesota Standards of Performance Applicability

- Sample list of Compliance Issues

- Sample Comments for commonly missing NSPS Tank Reporting

- CALCULATION NOTE – don’t use TANKS emissions estimation software for calculations

- Reference Vapor Pressure Tables

Sample TSD Language

New Source Performance Standards (NSPS)

The following New Source Performance Standards apply to the operations at this facility.

- 40 CFR pt. 60, subp. Kb,  Standards of Performance for Volatile Organic Liquid Storage Vessels (Including Petroleum Liquid Storage Vessels) for Which Construction, Reconstruction, or Modification Commenced After July 23, 1984

  - The facility was constructed in 1994, therefore all tanks were constructed after 1984.

  - The following tables provide the data used for determining applicability of the standard

Table 1: 40 CFR § 60.110b(a) Applicability and Exemptions

| Tank TEMPO ID DELTA ID AST ID | Capacity (gal)3 | Capacity (m3) | Material Stored | Max vapor pressure (kPa)1 | Is capacity ≥ 75 m3 (19813 gal) and constructed after July 23, 1984? If yes, check for exemptions in next 2 columns | Exemption: Is 75 m3 < capacity < 151 m3 (39900 gal) and VP < 15 kPa? OR >151 and vp<3.5 kPa? | Exemption: Is it a process tank as defined in 60.111b?2 | Is supb. Kb applicable, after exemptions? |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EQ 123 TK 003 1808 | 500,000 | 1892.7 | 200-proof Ethanol (E-100) | 6.3 kPa @ 22C/73F >5.2 kPa | Yes, Kb applies | No | No | YES |
| EQ152 TK001 Day-2 | 38,958 | 147.47 | 200-proof Ethanol (E-100) | 6.3 kPa @ 22C/73F >5.2 kPa (0.754 psi) | Yes, but… | Yes, exempt | Yes, exempt | NO |
| EQ156 TK003 PS-1 | 189,393 | 716.93 | Denatured Ethanol (E 95) | 6.3 kPa @ 22C/73F >5.2 kPa | Yes, Kb applies | No | No | YES |
| EQ153 TK004 Day-3 | 79,897 | 302.44 | 200-proof Ethanol (E-100) | 6.3 kPa @ 22C/73F >5.2 kPa | Yes, but… | No | Yes, exempt | NO |
| EQ154 TK005 DN-1 | 21,220 | 80.33 | Gasoline | > 27.6 kPa | Yes, Kb applies | No | No | YES |
| EQ151 TK008 190 | 86,947 | 329.13 | 190-proof Ethanol | 6.3 kPa @ 22C/73F >5.2 kPa | Yes, but… | No | Yes, exempt | NO |

1. Max. vapor pressure is defined as local maximum monthly average temperature as reported by the National Weather Service for VOL's stored at the ambient temperature. The vapor pressure used in the Tanks program is a different value based on a different averaging period. Typically July is the month with the maximum monthly average temperature. In Minnesota, that temperature would be around 73 degrees F/22 degrees C.

Need to get updated max. vp from Permittee (part of Kb notification), so you can populate the SI detail field in TEMPO.

2. See EPA determination dated 11/20/2007 Process Tanks Defined, Control Number: 0800041

3. Information for tanks in AQ and AST must be related in the Master File. Use the AST-AQ Tank Process checklist) to set up the relationship. The information in TEMPO (e.g., capacity, material) should be the same. If not, explain in TSD. For instance, Permittee may use a larger capacity for PTE calculations to be conservative. The checklist is linked in the Permit Checklist-Tempo, it can also be found at (X:\\databases\AQ\WKPLAN\PermitTeamDocuments\Tempo Checklists\Checklist References\AST-AQ tank process.

Table 2: 40 CFR § 60.112b(a) Standard for VOC requiring a floating roof

| Tank | Capacity (m3) | Material Stored | Max vapor pressure (kPa) 80F* | Is capacity > 151 m3 and max. VP ≥ 5.2 kPa and < 76.6 kPa? | Is 75 m3 ≤ capacity < 151 m3 and VP > 27.6 kPa? | Floating Roof Required? |
| --- | --- | --- | --- | --- | --- | --- |
| EQ 123 TK 003 1808 | 1892.7 | 200-proof Ethanol (E-100) | 6.3 >5.2 kPa | Yes | No | YES |
| EQ152 TK001 Day-2 | 147.47 | Ethanol (E-100) | 6.3 >5.2 kPa | Exempt | Exempt | Exempt |
| EQ156 TK003 PS-1 | 716.93 | Denatured Ethanol (E-95) | 6.3 >5.2 kPa | Yes | No | Yes |
| EQ153 TK004 Day-3 | 302.44 | Ethanol (E-100) | 6.3 >5.2 kPa | Exempt | Exempt | Exempt |
| EQ154 TK005 DN-1 | 80.33 | Gasoline | 51.021 > 27.6 kPa | No | Yes | Yes |
| EQ151 TK008 190 | 329.13 | 190-proof Ethanol (E-100) | 6.3 >5.2 kPa | Exempt | Exempt | Exempt |

*In Minnesota, the typical maximum monthly average temperature is in July, and is around 72 degrees F. It is expected that ethanol tanks in Minnesota will contain ethanol with a max vp > 5.2 kPa. See data tables at end of this document.

Note: For vessels operated above or below ambient temperatures, the maximum true vapor pressure is calculated based upon the highest expected calendar-month average of the storage temperature. For vessels operated at ambient temperatures, the maximum true vapor pressure is calculated based upon the maximum local monthly average ambient temperature as reported by the National Weather Service.

Table 3: 40 CFR § 60.112xx Tank Seal Description and NSPS Inspections

Information needed to write NSPS requirements, ensure compliance with NSPS requirements,

and populate Tempo database.

| Tank | Capacity (m3) | Seal | Previous Internal Inspection | Next Internal Inspection | AST permit Internal Inspection due date | MPCA permit action 010, COMG 2? | NSPS Internal Inspection due date |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EQ152 TK001 Day-2 | 147.47 | NA - Fixed Roof | - | - | 2014 | No - correct | Exempt |
| EQ155 TK002 DN-2 | 97.14 | Fixed Roof – needs control | - | - | Follow SP001 | No – error, add to GP | Within xx days of installation date. |
| EQ156 TK003 PS-1 | 716.93 | Vapor-mount w/ rim mount secondary | 2014 | 2024 | 2014 | Yes, remain in GP | 2024 |
|  | 302.44 | Vapor-mount w/ rim mount secondary | 2011 | 2021 | 2011 | Yes – error, remove from GP | Exempt |
| EQ154 TK005 DN-1 | 80.33 | Fixed Roof – needs control | - | - | Follow SP001 | No – error, add to GP | Within xx days of permit issuance |
| EQ157 TK006 PS-2 | 1035.20 | Vapor-mount w/ rim mount secondary | 2009 | 2019 | 2009 | Yes, remain in GP | 2019 |

NOTE: Permit xxxxxxxx-010, Group 002 Floating Roof Tanks Requirements. Tanks included in group are TK003, TK004, TK006, TK007 and TK008. Group should not include TK004 or TK008, should include TK002 and TK005.

Table 4: Minnesota Standards of Performance Applicability

Minn. R. 7011.1505 Standards of Performance for Storage Vessels and Minn. R. 7011.0715

All tanks constructed after 6/11/1973

| Tank | Capacity (m3) | Material Stored1 | True vapor pressure (psia) from TANKS | Is capacity > 2,000 gal and ≤40,000 gal? [subp. 3, B] | Is capacity > 40,000 gal and true vp >1.5 psia (10.34 kPa) and ≤11.1 psia (76.5kPa)? [subp. 3, C(1)] | Is capacity > 40,000 gal and true vp >11.1 psia (76.5kPa)? [subp. 3, C(2) | Comply with Minn. R. 7011.1505?2 | Comply with Minn. R. 7011.0715?3 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EQ152 TK001 Day-2 | 38,958 | Ethanol (E-100) | NA – applies to petroleum products | NA | NA | NA | No | Yes |
| EQ155 TK002 DN-2 | 25,661 | Gasoline | >10.34 kPa and <76.5 kPa | Yes | No | No | Yes, Subp. B (or C) | No |
| EQ156 TK003 PS-1 | 189,393 | Denatured Ethanol | 8.398 >5.2 kPa | No | No | No | No | No, subject to NSPS |
| EQ151 TK008 190 | 86,947 | 190-proof Ethanol | NA – applies to petroleum products | NA | NA | NA | No | Yes |

1.  MN SOP applies to petroleum-based liquids, it does not apply to tanks storing ethanol. This is determined by reading the definitions section in the rule.

2. A facility can be subject to both 40 CFR pt. 60, subp. Kb and Minn. R. 7011.1505.

3. Minn. R. 7011.0715 only applies if no other Standard of Performance (state or federal), applies.

Sample list of Compliance Issues:

- TK002 and TK005 are subject to 40 CFR pt. 60, subp. Kb. As such they are subject to control (e.g., an internal floating roof). The tanks currently have a fixed roof. Permit Action 010 did not identify the tanks as subject to control under the standard, this was an error that should be considered.

- Permittee did not submit initial NSPS notification, with accompanying reports for any of the tanks. The blanket “notification” received 10/25/2011 did not include the report (e.g., details of the controls).

  - For each storage vessel provide a report. Refer to enforcement.

- The fuel island (blender pumps, dispensing and 3 tanks) was installed in 1997, and was not identified as an emission unit in the permit, nor as an insignificant emission unit.

- Facility gasoline tanks for fueling facility equipment were not identified, need to add into permit. Fuel-dispensing emissions for tanks as small as 300 gallons can trigger injunctive relief provisions under PSD.

- Smaller tanks that include sulfur compounds or methanol (HAP, but not a VOC) may need to be listed as IA.

- Corrosion inhibitor tanks may typically be listed as IA.

Sample Comments for commonly missing NSPS Tank Reporting:

- For each storage vessel subject to 40 CFR pt. 60, subp. Kb, provide a report that describes the control equipment (the floating roof) and certifies that the control equipment meets the specification of §60.112b(a)(1) and §60.113b(a)(1). The description of the control equipment for each tank must contain enough detail to determine the compliance determination method for the tank (i.e. type of closure device). Neither the MPCA nor the EPA has any record of the initial notifications [as required by §60.7(a)(3)], nor the report that was to be attached to the initial notification as required by §60.112b(a)(1), with one exception.

- For each storage vessel subject to 40 CFR pt. 60, subp. Kb, provide a record of each inspection performed as required by §60.113b (a)(1), (a)(2), (a)(3), and (a)(4). The record must identify the storage vessel on which the inspection was performed and shall contain the date the vessel was inspected and the observed condition of each component of the control equipment (seals, internal floating roof, and fittings).

- For each storage vessel subject to 40 CFR pt. 60, subp. Kb, please provide a record which shows the dimension of the storage vessel and an analysis showing the capacity of the storage vessel as required by §60.116b(b).

- For each storage vessel subject to 40 CFR pt. 60, subp. Kb, please provide a copy of the record of the VOL stored, the period of storage, and the maximum true vapor pressure of that VOL during the respective storage period.

CALCULATION NOTE – don’t use TANKS emissions estimation software for calculations

From Air Mail October 2018

TANKS Emissions Estimation Software, Version 4.09d is no longer supported by EPA. EPA has stated that they have observed reliability issues, and anticipate further problems with the software, on more current Windows operating systems. Since the MPCA cannot verify emissions data from Tanks 4.09d, the agency will no longer be accepting emissions data using the software in permit applications. All existing, permitted tanks which were previously approved using the TANKS software will not be affected. Moving forward if the Permittee is installing a new tank, changing a tank’s substance, or increasing a tank’s throughput they should use the equations/algorithms from AP-42 Chapter 7 to calculate emissions from the units. These equations/algorithms can be employed with many current spreadsheet/software programs.

Vapor Pressure and Temperature charts for Ethanol

Typical average monthly high temperature in Minnesota: 73 degrees F = 22 degree C

https://www.engineeringtoolbox.com/vapor-pressure-d_312.html

Liquids - Vapor Pressure @ 22 degree C

Approximate vapor pressure for temperatures in the range 20 oC - 25 oC (68 oF - 77 oF).

https://www.engineersedge.com/fluid_flow/fluid_data.htm