## O&M History
Table 1
SYSTEM OPERATION AND MAINTENANCE SUMMARY
MN Bio Business Center
221 1st Avenue SW
Rochester, Minnesota
Date | Approximate Time | Sensophone Call Received? | Alarm Condition | DPE System Status | Comments
2009-04-09 | NA | NA | NA | Off | DPE system temporarty startup. Sampled initial DPE groundwater discharge and air emissions. System shut down to determine if air emissions and/or groundwater treatment were necessary.
2009-06-04 | NA | NA | NA | Off | Air stripper installed. Air stripper air emissions and influent and effluent groundwater samples collected.
2009-06-05 | NA | NA | NA | Off/On | Installed temporary secondary containment around DPE room door way. DPE system left on.
2009-06-06 | 19:00 | Y | MS High Level | On/Off
2009-06-08 | NA | NA | NA | Off | Landmark on site to clean MS float switch assembly. DPE system left off per client request until elevator pit drain tile sump can be connected to the air stripper, a permanent secondary containment berm can be installed, and additional floor sump alarm and conductivity meter can be installed.
2009-06-19 | NA | NA | NA | Off | Landmark onsite to monitor elevator pit sump water levels and PID readings.
2009-06-23 | NA | NA | NA | Off | Landmark, SDE, and Muska on site to install permanent secondary containment berm and sump pit flow meter.
2009-06-25 | NA | NA | NA | Off | Landmark and PLC on site to terminate switches to the control panel. Noticed lower trilevel float switch is getting caught on the site tube. PLC to replace MS trilevel float assembly. Pumped 300 gallons of water from elevator drain tile sump through the air stripper. Sump appears to be recharging with water.
2009-06-29 | NA | NA | NA | Off/On | Landmark replaced MS trilevel float assembly. Bottom float still catches on site tube; therefore, Landmark installed JB-welded washers onto float assembly. Also compared flow meter readings with handheld monitor; replaced leaking air stripper hoses; recorded all system data from gauges and control panel. System restarted for permanent operation.
2009-07-09 | NA | NA | NA | On | Landmark onsite to troubleshoot low flowrate and vacuum readings observed remotely, to collect fluid level measurements at each well, to check the vacuum influence from DPE-1 operation at each DPE well head location; collect operational data during operation of DPE-1; to conduct a groundwater recovery test a DPE-1; modified the drop tube at DPE-3; and collected operational data wile operating on DPE-3. Kept system operating on DPE-1. Sampled groundwater discharge.
2009-07-18 | NA | No | DPE Pump Motor Fault | On/Off
2009-07-20 | NA | NA | DPE Pump Motor Fault | Off | Received a call from Paramark stating the DPE was off and there was about 1 quart of oil leaking from the DPE pump.
2009-07-22 | NA | NA | DPE Pump Motor Fault | Off | Landmark onsite to troubleshoot DPE system shut down and determine the source of the oil leak.
2009-07-24 | NA | NA | DPE Pump Motor Fault | Off | Landmark and PLC onsite to remove DPE pump and deliver to John Henry Foster for Repair.
2009-08-11 | NA | NA | DPE Pump Motor Fault | Off/On | Landmark and PLC onsite to reinstall repaired DPE pump and restart the system. Landmark installed thermometer to monitor the ambient and max temperature in the DPE room in two different locations. Landmark swept, vacuumed, and mopped the floor several times to prevent dust from passing through the vacuum relief valve and clogging the pump inlet screen. PLC fixed the sensaphone. PLC and Landmark checked flow rate readings with blower curve. DPE system was restarted.
2009-08-14 | 13:17 | Y | DPE Pump High Inlet Vacuum | On/Off/On | Paramark opened all of the individual DPE well bleed valves and restarted the system.
2009-08-16 | 4:34 | Y | DPE Pump High Outlet Temperature | On/Off
2009-08-17 | NA | NA | DPE Pump High Outlet Temperature | Off/On | Paramark checked max room temperature readings and all were OK. Paramark could not restart the DPE system. Landmark onsite to troubleshoot the pump and determined the inlet screen was plugged. Landmark cleaned the inlet screen, replaced the moisture separator filter, and restarted the system. The system was adjusted to run with the DPE pump bleed valve open 5% and the DPE-1 bleed valve open 20%.
2009-08-18 | 4:15 | Y | DPE Pump High Inlet Vacuum | On/Off | Landmark tried restarting the system remotely, but the system would not operate for more than 30 seconds. A pressure drop was observed while trying to restart the system indicating the moisture separator filter or pump inlet screen was plugged.
2009-08-20 | NA | NA | DPE Pump High Inlet Vacuum | Off/On | Landmark onsite to troubleshoot system shutdown. Landmark verified the shutdown was the result of a plugged pump intake screen. The screen was cleaned with hydrochloric acid and reinstalled. Landmark installed a pipe plug in place of the vacuum relief valve to determine if the material plugging the screen is entering through the vacuum relief valve. Landmark added slits to DPE-1 drop tube to facilitate dewatering of the well. System restarted with DPE-1 bleed air valve opened 50% and pump bleed valve closed.
2009-08-22 | 5:30 | Y | DPE Pump High Inlet Vacuum | On/Off
2009-08-24 | NA | NA | DPE Pump High Inlet Vacuum | Off/On | Restarted system remotely. Directed Paramark to open DPE-1 bleed valve 100%.
2009-09-04 | NA | NA | NA | On | Landmark on site to conduct monthly monitoring and sampling event, install 1 micron moisture separator filter, and install new pump intake screen.
NA: Not Applicable.
Y: Yes.
N: No.