by Owner’s Consultant. Not certified by HGA.

Section 072623
Below-Grade Gas Retarder

PART 1 GENERAL

1.1 Summary

A. Below-grade gas retarder system for both vertical wall and sub slab gas retarder installation.
1. HDPE and LLDPE geomembranes with both smooth and textured surfaces.
B. Provide Work in accordance with the Voluntary Response Action Plan and the Environmental Contingency Plan for the Property as approved by the Minnesota Pollution Control Agency.
1.2 References

A. American Society for Testing and Materials (ASTM):

1. D 638, Standard Test Method for Tensile Properties of Plastics.

2. D 751, Standard Test Methods for Coated Fabrics. 

3. D 792, Standard Test Methods for Density and Specific Gravity (Relative Density) of Plastics by Displacement. 

4. D 1004, Standard Test Method for Initial Tear Resistance of Plastic Film and Sheeting.

5. D 1204, Standard Test Method for Linear Dimensional Changes of Non Rigid Thermoplastic Sheeting or Film at Elevated Temperature.

6. D 1238, Standard Test Method for Flow Rates of Thermoplastics by Extrusion Plastometer. 

7. D 1505, Standard Test Method for Density of Plastics by Density-Gradient Technique.

8. D 1603, Standard Test Method for Carbon Black in Olefin Plastics.

9. D 3895, Test Method for Oxidative Induction Time of Polyolefins by Thermal Analysis.

10. D 4218, Test Method for Determination of Carbon Black Content in Polyethylene Compounds by the Muffle-Furnace Technique.

11. D 4437, Standard Practice for Determining the Integrity of Field Seams Used in Joining Flexible Polymeric Sheet Geomembranes.

12. D 4833, Test Method for Index Puncture Resistance of Geotextiles, Geomembranes and Related Products. 

13. D 5199, Standard Test Method for Measuring Nominal Thickness of Smooth Geomembranes.

14. D 5397, Standard Test Method for Evaluation of Stress Crack Resistance of Polyolefins using Notched Constant Tensile Load Test. 

15. D 5596, Standard Practice for Microscopical Examination of Pigment Dispersion in Plastic Compounds. 

16. D 5641, Standard Practice for Geomembrane Seam Evaluation by Vacuum Chamber.

17. D 5721, Practice for Air-Oven Aging of Polyolefin Geomembranes.

18. D 5820, Test Method for Air Testing.

19. D 5885, Test Method for Oxidative Induction Time of Polyolefin Geosynthetics by High Pressure Differential Scanning Calorimetry.

20. D 5994, Standard Test Method for Measuring Nominal Thickness of Textured Geomembranes 

21. D 6365, Standard Practice for the Nondestructive Testing of Geomembrane Seams using The Spark Test

22. D5820-95, Pressurized Air Channel Test for Dual Seamed Geomembranes

B. Geosynthetic Research Institute (GRI):

1. GRI GM 9, Cold Weather Seaming of Geomembranes

2. GRI GM 10, The Stress Crack Resistance of HDPE Geomembrane Sheet

3. GRI GM 13, Test Properties, Testing Frequency for High Density Polyethylene (HDPE) Smooth and Textured Geomembranes

4. GRI GM 14, Test Frequencies for Destructive Seam Testing Selecting, variable intervals for taking geomembrane destructive samples using the method of attributes.

5. GRI GM 12, Measurement of the Asperity Height of Textured Geomembranes Using a Depth Gage

6. GRI GM 17, Test Methods, Test Properties and Testing Frequency for Linear Low Density Polyethylene (LLDPE) Smooth and Textured Geomembranes

7. GRI GM 19, Seam Strength and Related Properties of Thermally Bonded Polyolefin Geomembranes

1.3 Submittals

A. Submit under provisions of Section 01300, Submittals.

B. Documentation of manufacturer's qualifications. 

C. A material properties sheet, including at a minimum all properties specified in GRI GM 13, including test methods used. 

1. Sample of the material. 

2. Documentation of Installer's qualifications, as specified below.

a. Submit a list of at least ten completed facilities.  For each installation, provide: name and type of facility; its location; the date of installation; name and telephone number of contact at the facility; type and thickness of geomembrane and; surface area of the installed geomembrane. 

b. Submit resumes or qualifications of the Installation Supervisor, Master Seamer and Technicians to be assigned to this project.

c. Quality Control Program.

3. Example Material Warranty and Liner Installation Warranty 

D. Shop Drawings 

1. Submit copies of shop drawings for engineer's approval within a reasonable time so as not to delay the start of geomembrane installation.  Shop drawings shall show the proposed panel layout identifying seams and details.  Seams should generally follow the direction of the slope.  Butt seams or roll-end seams should not occur on a slope unless approved by the Owner's Representative.  Butt seams on a slope, if allowed, should be staggered.

2. Placement of geomembrane should not be allowed to proceed until Owner's Representative has received and approved the shop drawings.

E. Additional Submittals (In-Progress and at Completion) 

1. Manufacturer's warranty
2. Geomembrane installation warranty.

3. Daily written acceptance of subgrade surface. 

4. Low-temperature seaming procedures if applicable.

5. Prequalification test seam samples.

6. Field seam non-destructive test results.

7. Field seam destructive test results.

8. Daily field installation reports.

9. Installation record drawing.
F. Submit certification that the geomembrane and welding rod supplied for the project are made from the same material type and are compatible.
1.4 Quality Control

A. Manufacturer's Qualifications: The manufacturer of geomembrane of the type specified or similar product shall have at least five years experience in the manufacture of such geomembrane.  In addition, the geomembrane manufacturer shall have manufactured at least 1,000,000 square meters (10,000,000 square feet) of the specified type of geomembrane or similar product during the last five years.

B. Installer's Qualifications

1. The Geomembrane Installer shall be the Manufacturer, approved Manufacturer's Installer or a contractor approved by the Owner's Representative to install the geomembrane.

2. The Geomembrane Installer shall have at least three years experience in the installation of the specified geomembrane or similar.  The Geomembrane Installer shall have installed at least 10 projects involving a total of 500,000 square meters (5,000,000 square feet) of the specified type of geomembrane or similar during the last three years. 

3. Installation shall be performed under the direction of a field Installation Supervisor who shall be responsible throughout the geomembrane installation, for geomembrane panel layout, seaming, patching, testing, repairs, and all other activities of the Geomembrane Installer.  The Field Installation Supervisor shall have installed or supervised the installation and seaming of a minimum of 10 projects involving a total of 500,000 square meters (5,000,000  square feet) of geomembrane of the type specified or similar product.  

4. Seaming shall be performed under the direction of a Master Seamer (who may also be the Field Installation Supervisor or Crew Foreman) who has seamed a minimum of  300,000 square meters (3,000,000 square feet) of geomembrane of the type specified or similar product, using the same type of seaming apparatus to be used in the current project.  The Field Installation Supervisor and/or Master Seamer shall be present whenever seaming is performed.

5. All seaming, patching, other welding operations, and testing shall be performed by qualified technicians employed by the Geomembrane Installer.
C. Geomembrane Pre-Construction Meeting shall be held at the site prior to installation of the geomembrane.  At a minimum, the meeting shall be attended by the Geomembrane Installer, Owner, Owner’s representative (Engineer and/or CQA Firm), and the Earthwork Contractor.

1. Topics for this meeting shall include:
a. Health and Safety

b. Lines of authority and communication.  Resolution of any project document ambiguity.

c. Methods for documenting, reporting and distributing documents and reports.

d. Procedures for packaging and storing archive samples.

e. Review of time schedule for all installation and testing.

f. Review of panel layout and numbering systems for panels and seams including details for marking on geomembrane. 

g. Procedures and responsibilities for preparation and submission of as-built panel and seam drawings.

h. Temperature and weather limitations.  Installation procedures for adverse weather conditions.  Defining acceptable subgrade, geomembrane, or ambient moisture and temperature conditions for working during liner installation. 

i. Subgrade conditions, dewatering responsibilities and subgrade maintenance plan. 

j. Deployment techniques including allowable subgrade for the geomembrane.

k. Plan for controlling expansion/contraction and wrinkling of the geomembrane. 

l. Covering of the geomembrane and cover soil placement. 

m. Measurement and payment schedules. 

n. Responsibilities of each party.

2. The meeting shall be documented by a person designated at the beginning of the meeting and minutes shall be transmitted to all parties.

1.5 Delivery, Storage and Handling

A. Each roll of geomembrane delivered to the site shall be labeled by the manufacturer.  The label shall be firmly affixed and shall clearly state the manufacturer's name, product identification, material thickness, roll number, roll dimensions and roll weight.

B. Geomembrane shall be protected from mud, dirt, dust, puncture, cutting or any other damaging or deleterious conditions.

C. Rolls shall be stored away from high traffic areas.  Continuously and uniformly support rolls on a smooth, level prepared surface.


1.6 Project Conditions

A. Geomembrane should not be installed in the presence of standing water, while precipitation is occurring, during excessive winds, or when material temperatures are outside the limits specified in Section 3.03.

1.7 Warranty

A. The Geomembrane Installer shall guarantee the geomembrane installation against defects in the installation and workmanship for 1 year commencing with the date of final acceptance. 

PART 2 - PRODUCTS

2.1 Geomembrane (VR-6)
A. New membrane designed and manufactured specifically for intended use for this Work 
B. Geomembrane rolls shall be seamless, high density polyethylene (HDPE - Formulated Sheet Density ≥ 0.94g/cc) or linear low density polyethylene (LLDPE - Formulated Sheet Density ≤ 0.939 g/cc) containing no plasticizers, fillers or extenders and shall be free of holes, blisters or contaminants, and leak free verified by 100 percent n line spark or equivalent testing.  The geomembrane shall be supplied as a continuous sheet with no factory seams in rolls.  
C. The geomembrane will meet the property requirements as shown in Table A (GRI GM 13) or Table B (GRI GM 17)
D. The geomembrane seams shall meet the property requirements as shown in Table 2, (Attachment B) or as required by project specifications
2.2 Source Quality Control

A. Test methods and frequencies used by the manufacturer for quality control/quality assurance of the above geomembrane prior to delivery, shall be in accordance with GRI GM 13 for HDPE geomembrane or GRI GM 17 for LLDPE geomembrane, or modified as required for project specific conditions. 

PART 3 - EXECUTION

3.1 Subgrade Preparation

A. The subgrade shall be prepared in accordance with the project specifications.  The geomembrane subgrade shall be uniform and free of sharp or angular objects that may damage the geomembrane prior to installation of the geomembrane.

B. The Geomembrane Installer and Owner’s Representative shall inspect the surface to be covered with the geomembrane on each day's operations prior to placement of geomembrane to verify suitability. 

C. The Geomembrane Installer and Owner’s Representative shall provide daily written acceptance for the surface to be covered by the geomembrane in that day's operations.  The surface shall be maintained in a manner, during geomembrane installation, to ensure subgrade suitability. 

D. All subgrade damaged by construction equipment and deemed unsuitable for geomembrane deployment shall be repaired prior to placement of the geomembrane.  All repairs shall be approved by the Owner's Representative and the Geomembrane Installer.  This damage, repair, and the responsibilities of the contractor and Geomembrane Installer shall be defined in the preconstruction meeting.

3.2 Geomembrane Placement

A. No geomembrane shall be deployed until the applicable certifications and quality control certificates listed in subsection 1.03 of this Section are submitted to and approved by the Owner's Representative within the timeframe specified in the Contract Documents.  If the material does not meet project specifications it shall be removed from the work area.

B. The geomembrane shall be installed below grade on vertical walls and beneath the slab to the limits shown on the project drawings included in the MPCA approved VRAP. 

C. No geomembrane material shall be unrolled and deployed if the material temperatures are lower than 0 degrees C (32 degrees F) unless otherwise approved by the Owner's Representative.  The specified minimum temperature for material deployment may be adjusted by the Owner’s Representative. Temperature limitations should be defined in the preconstruction meeting.  Typically, only the quantity of geomembrane that will be anchored and seamed together in one day should be deployed.

D. No vehicular traffic shall travel on the geomembrane other than an approved low ground pressure Vehicle or equivalent. 

E. Sand bags or equivalent ballast shall be used as necessary to temporarily hold the geomembrane material in position under the foreseeable and reasonably - expected wind conditions.  Sand bag material shall be sufficiently close- knit to prevent soil fines from working through the bags and discharging on the geomembrane.

F. Geomembrane placement shall not be done if moisture prevents proper subgrade preparation, panel placement, or panel seaming.  Moisture limitations should be defined in the preconstruction meeting.

G. Damaged panels or portions of the damaged panels which have been rejected shall be marked and their removal from the work area recorded.

H. The geomembrane shall not be allowed to "bridge over" voids or low areas in the subgrade. The geomembrane shall rest in intimate contact with the subgrade.

I. Wrinkles caused by panel placement or thermal expansion should be minimized in accordance with section 1.09  B11.

J. Considerations on Site Geometry: In general, seams shall be oriented parallel to the line of the maximum slope.  In corners and odd shaped geometric locations, the total length of field seams shall be minimized.  Seams shall not be located at low points in the subgrade unless geometry requires seaming at such locations and if approved by the Owner's Representative.

K. Overlapping:  Any barrier joints/seams, both lateral and butt, shall be overlapped at least 12 inches and in accordance with manufacturer’s recommended seam completion and testing procedures.
L. Vertical Wall Instructions:

1. Install an approved waterproofing membrane according to the manufacturer’s installation instructions.  This may include sheet goods, or liquid applied membranes be they roll, brush or spray. 

2. While the membrane is still tacky, install the geomembrane.  Use a termination bar with concrete nails at the termination of the water proofing membrane.

3. Supervised care shall be taken during back filling against the material so that it is n ot damaged or punctured.  If damage occurs, patch using the techniques outlined above.    
3.3 Seaming Procedures

A. Cold weather installations should follow guidelines as outlined in GRI GM9.

B. No geomembrane material shall be seamed when liner temperatures are less than 0 degrees C (32 degrees F) unless the following conditions are complied with:

1. Seaming of the geomembrane at material temperatures below 0 degrees C (32 degrees F) is allowed if the Geomembrane Installer can demonstrate to the Owner's Representative, using pre-qualification test seams, that field seams comply with the project specifications, the safety of the crew is ensured, and geomembrane material can be fabricated (i.e. pipeboots, penetrations, repairs. etc.)  at sub-freezing temperatures.

2. The Geomembrane Installer shall submit to the Owner's Representative for approval, detailed procedures for seaming at low temperatures, possibly including the following: 

a. Preheating of the geomembrane 

b. The provision of a tent or other device if necessary to prevent heat losses during seaming and rapid heat losses subsequent to seaming.

c. Number of test welds to determine appropriate seaming parameters

C. No geomembrane material shall be seamed when the sheet temperature is above 75 degrees C (170 degrees F) as measured by an infrared thermometer or surface thermocouple unless otherwise approved by the Owner's Representative.  This approval will be based on recommendations by the manufacturer and on a field demonstration by the Geomembrane Installer using prequalification test seams to demonstrate that seams comply with the specification.

D. Seaming shall primarily be performed using automatic fusion welding equipment and techniques.  Extrusion welding shall be used where fusion welding is not possible such as at pipe penetrations, patches, repairs and short (less than a roll width) runs of seams.

E. Fishmouths or excessive wrinkles at the seam overlaps shall be minimized and when necessary cut along the ridge of the wrinkles back into the panel so as to effect a flat overlap.  The cut shall be terminated with a keyhole cut (nominal 10 mm (1/2 in) diameter hole) so as to minimize crack/tear propagation. The overlay shall subsequently be seamed. The key hole cut shall be patched with an oval or round patch of the same base geomembrane material extending a minimum of 150 mm (6 in.) beyond the cut in all directions.

3.4 Pipe and Structure Penetration Sealing System

A. Complete penetration and pipe sealing system as recommended by the manufacturer.

B. Penetrations shall be constructed from the base geomembrane material, flat stock, prefabricated boots and accessories as recommended by the manufacturer.  The pre-fabricated or field fabricated assembly shall be field welded to the geomembrane as recommended by the manufacturer so as to prevent leakage. This assembly shall be tested.  Where field non destructive testing can not be performed, attachments will be field spark tested by standard holiday leak detectors in accordance with ASTM 6365

C. Spark testing should be done in areas where both air pressure testing and vacuum testing are not possible.

1. Equipment for Spark testing shall be comprised of but not limited to: A hand held holiday spark tester and conductive wand that generates a high voltage.

2. The testing activities shall be performed by the Geomembrane Installer by placing an electrically conductive tape or wire beneath the seam prior to welding. A trial seam containing a non welded segment shall be subject to a calibration test to ensure that such a defect (non welded segment) will be identified under the planned machine settings and procedures. Upon completion of the weld, enable the spark tester and hold approximately 25mm (1 in) above the weld moving slowly over the entire length of the weld in accordance with ASTM 6365. If there is no spark the weld is considered to be leak free.

3. A spark indicates a hole in the seam. The faulty area shall be located, repaired and retested by the Geomembrane Installer.

4. Care should be taken if flammable gases are present in the area to be tested.

3.5 Field Quality Control

A. The Owner’s Representative shall be notified prior to all pre qualification and production welding and testing, or as agreed upon in the pre construction meeting.

B. Prequalification Test Seams

1. Test seams shall prepare and tested by the Geomembrane Installer to verify that seaming parameters (speed, temperature and pressure of welding equipment) are adequate.  

2. Test seams shall be made by each welding technician and tested in accordance with ASTM D 4437 at the beginning of each seaming period.  Test seaming shall be performed under the same conditions and with the same equipment and operator combination as production seaming.  The test seam shall be approximately 3.3 meters (10 feet) long for fusion welding and 1 meter (3 feet) long for extrusion welding with the seam centered lengthwise. At a minimum, tests seams should be made by each technician 1 time every 4–6 hours; additional tests may be required with changes in environmental conditions.

3. Two 25 mm (1 in) wide specimens shall be die-cut by the Geomembrane Installer from each end of the test seam.  These specimens shall be tested by the Geomembrane Installer using a field tensiometer testing both tracks for peel strength and also for shear strength.  Each specimen should fail in the parent material and not in the weld, “Film Tear Bond"(F.T.D. failure). Seam separation equal to or greater than 25 percent of the track width shall be considered a failing test. 

4. The minimum acceptable seam strength values to be obtained for all specimens tested as specified.  Four specimens shall pass for the test seam to be a passing seam. 

5. If a test seam fails, an additional test seam shall be immediately conducted.  If the additional test seam fails, the seaming apparatus shall be rejected and not used for production seaming until the deficiencies are corrected and a successful test seam can be produced.

6. A sample from each test seam shall be labeled.  The label shall indicate the date, geomembrane temperature, number of the seaming unit, technician performing the test seam and pass or fail description.  The sample shall then be given to the Owner's Representative for archiving.

C. Field Seam Non-destructive Testing

1. All field seams shall be non-destructively tested by the Geomembrane Installer over the full seam length before the seams are covered.  Each seam shall be numbered or otherwise designated.  The location, date, test unit, name of tester and outcome of all non-destructive testing shall be recorded and submitted to the Owner's Representative.

2. Testing should be done as the seaming work progresses, not at the completion of all field seaming, unless agreed to in advance by the Owner's Representative.  All defects found during testing shall be numbered and marked immediately after detection.  All defects found should be repaired, retested and remarked to indicate acceptable completion of the repair.

3. Non-destructive testing shall be performed using vacuum box, air pressure or spark testing equipment. 

4. Non-destructive tests shall be performed by experienced technicians familiar with the specified test methods.  The Geomembrane Installer shall demonstrate to the Owner's Representative all test methods to verify the test procedures are valid.

5. Extrusion seams shall be vacuum box tested by the Geomembrane Installer in accordance with ASTM D 4437 and ASTM D 5641 with the following equipment and procedures:

a. Equipment for testing extrusion seams shall be comprised of but not limited to: a vacuum box assembly consisting of a rigid housing, a transparent viewing window, a soft rubber gasket attached to the base, port hole or valve assembly and a vacuum gauge; a vacuum pump assembly equipped with a pressure controller and pipe connections; a rubber pressure/vacuum hose with fittings and connections; a plastic bucket; wide paint brush or mop; and a soapy solution. 

b. The vacuum pump shall be charged and the tank pressure adjusted to approximately 35 kPa (5 psig).

c. The Geomembrane Installer shall create a leak tight seal between the gasket and geomembrane interface by wetting a strip of geomembrane approximately  0.3m (12 in) by 1.2m  (48 in)  (length and width of box) with a soapy solution, placing the box over the wetted area, and then compressing the box against the geomembrane.  The Geomembrane Installer shall then close the bleed valve, open the vacuum valve, maintain initial pressure of approximately 35 kPa (5 psig) for approximately 5 seconds. The geomembrane should be continuously examined through the viewing window for the presence of soap bubbles, indicating a leak.  If no bubbles appear after 5 seconds, the area shall be considered leak free.  The box shall be depressurized and moved over the next adjoining area with an appropriate overlap and the process repeated.  

d. All areas where soap bubbles appear shall be marked, repaired and then retested. 

e. At locations where seams cannot be non destructively tested, such as pipe penetrations, alternate nondestructive spark testing as specified or equivalent should be substituted. 

f. All seams that are vacuum tested shall be marked with the date tested, the name of the technician performing the test and the results of the test. 

6. Double Fusion seams with an enclosed channel shall be air pressure tested by the Geomembrane Installer in accordance with ASTM D 5820 and ASTM D 4437 and the following equipment and procedures:

a. Equipment for testing double fusion seams shall be comprised of but not limited to: an air pump equipped with a pressure gauge capable of generating and sustaining a pressure of 210 kPa (30 psig), mounted on a cushion to protect the geomembrane; and a manometer equipped with a sharp hollow needle or other approved pressure feed device.

b. The Testing activities shall be performed by the Geomembrane Installer.  Both ends of the seam to be tested shall be sealed and a needle or other approved pressure feed device inserted into the tunnel created by the double wedge fusion weld.  The air pump shall be adjusted to a pressure of 210 kPa (30 psig), and the valve closed,. Allow 2 minutes for the injected air to come to equilibrium in the channel, and sustain pressure for 5 minutes. If pressure loss does not exceed 28 kPa (4 psig) after this five minute period the seam shall be considered leak tight.  Release pressure from the opposite end verifying pressure drop on needle to ensure testing of the entire seam. The needle or other approved pressure feed device shall be removed and the feed hole sealed.  

c. If loss of pressure exceeds 28 kPa (4 psig) during the testing period or pressure does not stabilize, the faulty area shall be located, repaired and retested by the Geomembrane Installer.

d. Results of the pressure testing shall be recorded on the liner at the seam tested and on a pressure testing record. 

D. Destructive Field Seam Testing 

1. One destructive test sample per 150 linear m (500 linear ft) seam length or another predetermined length in accordance with GRI GM 14 shall be taken by the Geomembrane Installer from a location specified by the Owner's Representative.  The Geomembrane Installer shall not be informed in advance of the sample location.  In order to obtain test results prior to completion of geomembrane installation, samples shall be cut by the Geomembrane Installer as directed by the Owner's Representative as seaming progresses.

2. All field samples shall be marked with their sample number and seam number.  The sample number, date, time, location, and seam number shall be recorded.  The Geomembrane Installer shall repair all holes in the geomembrane resulting from obtaining the seam samples.  All patches shall be vacuum box tested or spark tested.  If a patch cannot be permanently installed over the test location the same day of sample collection, a temporary patch shall be tack welded or hot air welded over the opening until a permanent patch can be affixed.

3. The destructive sample size shall be 300 mm (12 in) wide by 1 m (36 in) long with the seam centered lengthwise.  The sample shall be cut into three equal sections and distributed as follows: one section given to the Owner's Representative as an archive sample; one section given to the Owner's Representative for laboratory testing as specified in paragraph 5 below; and one section retained by the Geomembrane Installer for field testing as specified in paragraph 4 below. 

4. For field testing, the Geomembrane Installer shall cut 10 identical 25 mm (1 in) wide replicate specimens from his sample.  The Geomembrane Installer shall test five specimens for seam shear strength and five for peel strength. Peel tests will be performed on both inside and outside weld tracks. To be acceptable, 4 of 5 test specimens must pass the stated criteria in section 2.02 with less than 25 percent separation.  If 4 of 5 specimens pass, the sample qualifies for testing by the testing laboratory if required. 

5. If independent seam testing is required by the specifications it shall be conducted in accordance with ASTM 5820 or ASTM D4437 or GRI GM 6.

6. Reports of the results of examinations and testing shall be prepared and submitted to the Owner's Representative.

7. For field seams, if a laboratory test fails, that shall be considered as an indicator of the possible inadequacy of the entire seamed length corresponding to the test sample.  Additional destructive test portions shall then be taken by the Geomembrane Installer at locations indicated by the Engineer; typically 3 m (10 ft) on either side of the failed sample and laboratory seem tests shall be performed.  Passing tests shall be an indicator of adequate seams.  Failing tests shall be an indicator of non-adequate seams and all seams represented by the destructive test location shall be repaired with a cap-strip extrusion welded to all sides of the capped area.  All cap-strip seams shall be non-destructively vacuum box tested until adequacy of the seams is achieved.  Cap strip seams exceeding 50 M in length (150 FT) shall be destructively tested.

E. Identification of Defects

1. Panels and seams shall be inspected by the Installer and Owner's Representative during and after panel deployment to identify all defects, including holes, blisters, undispersed raw materials and signs of contamination by foreign matter. 

F. Evaluation of Defects: Each suspect location on the liner (both in geomembrane seam and non-seam areas) shall be non-destructively tested using one of the methods specified.  Each location which fails non-destructive testing shall be marked, numbered, measured and posted on the daily "installation" drawings and subsequently repaired.

1. If a destructive sample fails the field or laboratory test, the Geomembrane Installer shall repair the seam between the two nearest passed locations on both sides of the failed destructive sample location.

2. Defective seams, tears or holes shall be repaired by reseaming or applying a extrusion welded cap strip.

3. Reseaming may consist of either: 

a.  Removing the defective weld area and rewelding the parent material using the original welding equipment; or

b. Reseaming by extrusion welding along the overlap at the outside seam edge left by the fusion welding process.

4. Blisters, larger holes, and contamination by foreign matter shall be repaired by patches and/or extrusion weld beads as required.  Each patch shall extend a minimum of 150 mm (6 in) beyond all edges of the defects. 

5. All repairs shall be measured, located and recorded.

G. Verification of Repairs on Seams: Each repair shall be non-destructively tested using either vacuum box or spark testing methods.  Tests which pass the non-destructive test shall be taken as an indication of a successful repair.  Failed tests shall be reseamed and retested until a passing test results.  The number, date, location, technician and test outcome of each patch shall be recorded.

H. Daily Field Installation Reports: At the beginning of each day's work, the Installer shall provide the Engineer with daily reports for all work accomplished on the previous work day.  Reports shall include the following: 

1. Total amount and location of geomembrane placed;

2. Total length and location of seams completed, name of technicians doing seaming and welding unit numbers;


3. Drawings of the previous day's installed geomembrane showing panel numbers, seam numbers and locations of non-destructive and destructive testing;

4. Results of pre-qualification test seams; 

5. Results of non-destructive testing; and 

6. Results of vacuum testing of repairs.

7. Destructive test results shall be reported prior to covering of liner or within 48 hours.

3.6 Disposal of Scrap Materials

A. On completion of installation, the Geomembrane Installer shall dispose of all trash and scrap material in a location approved by the Owner, remove equipment used in connection with the work herein, and shall leave the premises in a neat acceptable manner.  No scrap material shall be allowed to remain on the geomembrane surface.
Attachment A.
Table 1(a) – Seam Strength and related Properties of Thermally Bonded Smooth and Textured Linear Low Density Polyethylene (LLDPE) Geomembrane (English Units)

	Geomembrane Nominal Thickness
	20 mils
	30 

mils
	40 

mils
	50

 mils
	60

 mils
	80

 mils
	100

 mils
	120 

mils

	Hot Wedge Seams (1)

shear strength(2), lb/in.

shear elongation at break(3) , %

peel strength (2), lb/in.

peel separation, %
	30

50

25

25
	45

50

38

25
	60

50

50

25
	75

50

63

25
	90

50

75

25
	120

50

100

25
	150

50

125

25
	180

50

150

25

	Extrusion Fillet Seams (1)

shear strength(2), lb/in.

shear elongation at break(3) , %

peel strength (2), lb/in.

peel separation, %
	30

50

25

25
	45

50

34

25
	60

50

44

25
	75

50

57

25
	90

50

66

25
	120

50

88

25
	150

50

114

25
	180

50

136

25


Table 1(b) – Seam Strength and related Properties of Thermally Bonded Smooth and Textured Linear Low Density Polyethylene (LLDPE) Geomembrane (S.I. Units)

	Geomembrane Nominal Thickness
	0.50 

mm
	    0.75

 mm
	   1.0 

mm
	1.25

 mm
	1.5

 mm
	2.0

 mm
	2.5

 mm
	3.0 

mm

	Hot Wedge Seams (1)

shear strength(2), N/25mm

shear elongation at break(3) , %

peel strength (2), N/25mm

peel separation, %
	131

50

109

25
	197

50

166

25
	263

50

219

25
	328

50

276

25
	394

50

328

25
	525

50

438

25
	657

50

547

25
	788

50

657

25

	Extrusion Fillet Seams (1)

shear strength(2), N/25mm

shear elongation at break(3) , %

peel strength (2), N/25mm

peel separation, %
	131

50

95

25
	197

50

150

25
	263

50

190

25
	328

50

250

25
	394

50

290

25
	525

50

385

25
	657

50

500

25
	788

50

595

25


Notes for Tables 1(a) and 1(b):

1. Also for hot air and ultrasonic seaming methods

2. Value listed for shear and peel strength are for 4 out of 5 test specimens; the 5th specimen can be low as 80% of the listed values

3. Elongation measurements should be omitted for field testing
	Geomembrane Nominal Thickness
	30

 mils
	40 

mils
	50

 mils
	60 

mils
	80

 mils
	100

 mils
	120

 mils

	Hot Wedge Seams (1)

shear strength(2), lb/in.

shear elongation at break(3) , %

peel strength (2), lb/in.

peel separation, %
	57

50

45

25
	80

50

60

25
	100

50

76

25
	120

50

91

25
	160

50

121

25
	200

50

151

25
	240

50

181

25

	Extrusion Fillet Seams (1)

shear strength(2), lb/in.

shear elongation at break(3) , %

peel strength (2), lb/in.

peel separation, %
	57

50

39

25
	80

50

52

25
	100

50

65

25
	120

50

78

25
	160

50

104

25
	200

50

130

25
	240

50

156

25


Table 2(a) – Seam Strength and related Properties of Thermally Bonded Smooth and Textured linear High Density Polyethylene (HDPE) Geomembrane (English Units)

Table 2(b) – Seam Strength and related Properties of Thermally Bonded Smooth and Textured High Density Polyethylene (HDPE) Geomembrane (S.I. Units)

	Geomembrane Nominal Thickness
	0.75

 mm
	1.0 

mm
	1.25 

mm
	1.5

 mm
	2.0

 mm
	2.5

 mm
	3.0 

mm

	Hot Wedge Seams (1)

shear strength(2), N/25mm

shear elongation at break(3) , %

peel strength (2), N/25mm

peel separation, %
	250

50

197

25
	350

50

263

25
	438

50

333

25
	525

50

398

25
	701

50

530

25
	876

50

661

25
	1050

50

793

25

	Extrusion Fillet Seams (1)

shear strength(2), N/25mm

shear elongation at break(3) , %

peel strength (2), N/25mm

peel separation, %
	250

50

170

25
	350

50

225

25
	438

50

285

25
	525

50

340

25
	701

50

455

25
	876

50

570

25
	1050

50

680

25


Notes for Tables 2(a) and 2(b):

1. Also for hot air and ultrasonic seaming methods

2. Value listed for shear and peel strength are for 4 out of 5 test specimens; the 5th specimen can be low as 80% of the listed values

3. Elongation measurements should be omitted for field testing







Minnesota Bio-Business Center Building
Below-Grade Gas Retarder
and 3rd Street Parking Ramp Expansion
September 14, 2007
072623 - 12
1009-018-00 & 1009-019-00 (CP-2) CD

